Table of Contents

Introduction	2

Open Loop Settings for Fortress Batteries with Schneider Inverters	3

Open Loop Settings with Schneider Charge Controllers	5

Closed-Loop Setup between Fortress Batteries and Schneider Conext Gateway/ Insight Facility	6

Closed-Loop Setup between Fortress Batteries and Schneider Insight Home	7

Appendix	9

Exhibit A	9

Exhibit B	10

Exhibit C	11

Exhibit D	12

Exhibit E	13

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

Error! Hyperlink reference not valid.

# Introduction

This integration guide will help set up the charge/discharge parameters of Fortress Power batteries as they relate to Schneider inverters, as well as the setup of closed-loop communication between the Fortress batteries and Schneider inverters. Please note that only the Schneider XW Pro and Gateway support running the batteries in closed loop communication mode, and that the inverters will still need to be programmed in the open loop settings before setting up closed loop communication.

For any additional help, please contact techsupport@fortresspower.com

# Open Loop Settings for Fortress Batteries with Schneider Inverters

| Charger Setting > Custom Setting |  |  |  |
| --- | --- | --- | --- |
|  | 80% DoD, 6000 cycles | 90% DoD, 3000 cycles |  |
| Battery Type | Custom |  |  |
| Charge Cycle | 2StgNoFloat |  |  |
| Bulk Voltage | 54.4 V |  | 54.6 V |
| Max Bulk Current | eFlex:55A per battery eVault:100A per battery eVault MAX 150 per battery LFP-10: 70A per battery | eFlex: 60A per battery eVault:150A per battery eVault MAX: 180A per battery LFP-10: 80A per battery |  |
| Max Discharge Current | eFlex: 60A per battery eVault: 160A per battery eVault MAX: LFP-10: 100A per battery |  |  |
| Battery Capacity | eFlex: 105AH per battery eVault: 360AH per battery eVault MAX: 360AH per battery LFP-10: 200AH per battery |  |  |
| Max Charge Rate Percentage (%) | eFlex:60A per battery eVault:100A per battery eVault MAX 150 per battery LFP-10: 70A per battery Divided by Total Inverter DC Amperage |  | eFlex: 60A per battery eVault:150A per battery eVault MAX: 180A per battery LFP-10: 80A per battery Divided by Total Inverter DC Amperage |
| Default Battery Temperature | Warm |  |  |
| Recharge Volts | 51.3 |  |  |
| Grid Support Volts** | 53 |  |  |
| Absorb Volts | 54.4 |  |  |
| Absorb Time | 1 Hour |  |  |
| Charge Block Start | Default |  |  |
| Charge Block Stop | Default |  |  |
| Advanced Settings > Inverter Settings |  |  |  |
| Low Battery Cut Out Voltage | 48V (50V if allowed) |  |  |
| LBCO Hysteresis | 2.0V |  |  |
| LBCO Delay | 5 Sec |  |  |
| High Battery Cut Out Voltage | 61V (58V if allowed) |  |  |
| Search Watts | Default |  |  |
| Search Delay | Default |  |  |

**The Parameter Setting for Grid-tie Sell Mode:
In a DC coupled system, Grid Support or Enhanced Grid Support mode supplies PV power to the loads and sells surplus power to the grid. This mode of operation keeps the batteries as completely charged as possible.  The Enhanced Grid Support only works with lead acid batteries, please disable it when you use Fortress batteries.

Grid Support Mode is used for the systems with DC Sources not communication over Xanbus.

| Advanced Setting > Inverter Settings |  |
| --- | --- |
| Charger | Enabled |
| Enhanced Grid Support | N/A |
| Grid Support | 54V (site specific) |
| Recharge Volts | 51.3 V |
| Sell Mode | Enabled |
| Max Sell Amps** | PV array size ÷ 240V ÷ total inverter output kW |
| Advanced Setting > Charger Setting |  |
| Recharge Volts | 51.3 V |

** For example, if the system has a 10 KW PV array and 2 of XW+ 5848 inverters, the Max Sell Amps per inverter will be 10,000W/240V/2 = 21A

Grid Support Voltage Note: The grid support voltage will “sell back” the battery to the grid side of the battery inverter when voltage meets the programmed threshold. This is a user specific setting – some users will want to use more battery capacity for selling back, and others will want a full battery before selling back. Selling back at 54V will keep the battery mostly full. Users on reliable power grids wanting to sell back for evening peak utility rates may prefer to lower grid support to allow the battery to more deeply discharge at night (suggestion:52.5V).

Recharge Voltage Note: A battery voltage near 51.4V indicates an approximate 20% state of charge. As such, the inverter is programmed to recharge the battery from an AC power source (grid or generator) when the battery reaches a 20% SoC. This voltage setting can be increased to allow for more reserve capacity in the battery.

AC-coupled note: AC coupling an appropriately sized solar array on the backup side of the Schneider inverter will automatically charge the batteries. AC-coupling on the grid or supply side of the Schneider inverter will charge the batteries only when the battery bank reaches the inverter recharge voltage.

# Open Loop Settings with Schneider Charge Controllers

Parameter Setting for Fortress Batteries with Schneider XW+ MPPT 60/80

| Advanced Setting > Charger Setting |  |  |
| --- | --- | --- |
| Battery Type | Custom |  |
| Custom Setting |  |  |
|  | 80% DoD, 6000 cycles | 90% DoD, 3000 cycles |
| Charge Mode | 3 Stage |  |
| Eqlz Support | Disabled |  |
| Bulk Voltage | 54.4 V | 54.6 V |
| Absorb Voltage | 54.4 V | 54.6 V |
| Absorb Time | 60 minutes |  |
| Float Voltage | 54.4 V |  |
| Battery Temperature Compensation | 0mV/C |  |
| Battery Capacity | eFlex: 105AH per battery eVault: 360AH per battery eVault MAX: 360AH per battery LFP-10: 200AH per battery |  |
| Max Charge Rate Percentage* | eFlex:55A per battery eVault:100A per battery eVault MAX: 150A per battery LFP-10: 70A per battery Divide by total CC amp output | eFlex: 60A per battery eVault:150A per battery eVault MAX: 180A per battery LFP-10: 80A per battery Divide by total CC amp output |
| Charge Cycle | Warm |  |
| Recharge Volts | 53 V |  |
| Absorb Time | 1 Hour |  |
| Default Battery Temperature | Warm |  |
| Battery Voltage (Auto-detected) | 48V |  |

Note: The charge controllers can be set to a 3 stage charging cycle, but the inverter should be kept in a 2 stage charging cycle. Doing so, as well as setting the charge controller recharge voltage to be greater than that of the inverter recharge voltage, will prioritize charge controller charging over the inverter charging. Inverter charging is a grid/generator charge which has a lower priority than solar charge controller charging.

# Closed-Loop Setup between Fortress Batteries and Schneider Conext Gateway/ Insight Facility

All Fortress Power batteries work in open-loop communication mode—that is, with voltage detection. Closed loop does not exempt the installer from programming the inverter manually. Open loop settings should be programmed before setting up closed loop communication. The inverter will revert to open loop settings if closed loop communication drops.

- Connect communication cables and canbus terminator between the batteries

  - eFlex-specific instructions:

    - RX/TX ports are universal

    - The “master” battery is the one powered up first – so after plugging in the communication cables, turn the battery which will communicate to the Schnieder inverter on first. After the light show completes, push button the next eFlex battery on, proceeding down the chain to the last eFlex with the Canbus terminator. and install a Canbus communicator at the enda CAT6 cable into the eFlex and then into the RJ46 pinout converter (Exhibit A).

  - eVault-specific instructions:

    - Use the TX port on the master inverter to connect to the RX port of the slave inverter.

    - The inverter communication will therefore be plugged into the RX port of the master inverter.

  - eVault MAX specific instructions:

    - set the battery protocol to 1 on the touchscreen

    - plug the RJ45 cable into the battery RS485 port.

    - If three or more batteries are connected in parallel, turn on the 120Ω on the first and last battery. Leave the rest off.

- Modify the communication cable between the master battery and the inverter

  - eFlex-specific instructions:

    - Cut off one end of the ethernet cable and connect wire 7 (brown-white/RJ485A) to port 18 and pin 8 (brown/RJ485B) to port 20 on the Conext Gateway/ Insight Facility (Exhibit B).

  - eVault-&eVault MAX specific instructions:

    - Identify if the RJ45 cable is the A or B format. Typically, the cables are B format. Whichever format, the eVault uses wire 3+5 for RJ485A/B communication.

    - Cut off one end of the ethernet cable and connect wire 3 (typically green-white) to port 18 and wire 5 (typically blue-white) to port 20 on the Conext Gateway/ Insight Facility (Exhibit A).

- Power on the batteries and Schneider as usual and connect to the Conext Insight.

- Navigate to Setup -> Device Detection and run detection for RS-485-1 with range 1 to 2. The battery BMS will then appear in the device list, as the Schneider Battery Monitor (Exhibit C).

- Navigate to the Devices -> Inverter\Charger -> Configuration -> Advanced 
Charger settings should be set to lithium-ion battery with an charge cycle set to external BMS.
Grid Support settings should be set to state of charge control
Battery Management System settings should be set to Fault on Loss of BMS Status and loss of State of Charge information. (Exhibit D)

- Navigate to the Schneider Devices -> BMS Menu -> Battery Bank 1 -> Apply
Make sure the BMS is associated with Battery Bank 1 by clicking “Apply” (Exhibit E)

# Closed-Loop Setup between Fortress Batteries and Schneider Insight Home

- Repeat steps 1-2 from “Closed-Loop Setup between Fortress Batteries and Schneider Conext Gateway/ Insight Facility”.

- Modify the communication cable between the master battery and the inverter.

- eFlex-specific instructions:

- Cut off one end of the ethernet cable and connect wire 7 (brown white/RJ485A) to port 9 and pin 8 (brown/RJ485B) to port 11 on the Insight Home (Exhibit B).

- eVault-& eVault MAX specific instructions:

- Identify if the RJ45 cable is the A or B format. Typically, the cables are B format. Whichever format, the eVault uses wire 3+5 for RJ485A/B communication.

- Cut off one end of the ethernet cable and connect wire 3 (typically green-white) to port 9 and wire 5 (typically blue-white) to port 11 on the Insight Home (Exhibit B).

# Repeat steps 3-6 from “Closed-Loop Setup between Fortress Batteries and Schneider Conext Gateway/ Insight Facility”.

Closed Loop Communication Set-Up using Schneider Gateway

## Appendix

## Exhibit A

From Battery 		eFlex                                   eVault

Gateway Port 18     brown-white, wire 7         typ. green-white, wire 3

Gateway Port 20      brown RJ45,  wire 8           typ. blue-white, wire 5

Note: eValts delivered prior to 1/1/2021 need to use 
green-white for Gateway Port 18 and blue-white for Gateway Port 20

From Battery 		eFlex                                   eVault

Gateway Port 18     brown-white, wire 7         typ. green-white, wire 3

Gateway Port 20      brown RJ45,  wire 8           typ. blue-white, wire 5

Schneider Closed Loop Communication Set-Up using Insight Home

## Exhibit B

From Battery 		eFlex                                         eVault

Gateway Port 9        brown-white, wire 7                 green-white, wire 3

Gateway Port 11      brown, wire 8                              blue-white, wire 5

From Battery 		eFlex                                         eVault

Gateway Port 9        brown-white, wire 7                 green-white, wire 3

Gateway Port 11      brown, wire 8                              blue-white, wire 5

## Exhibit C

Appears after successful device detection

## Exhibit D

Charge controller recharge voltage should be set higher.

Note: 105 Amp hours per EFLEX

51.5

[Grab your reader’s attention with a great quote from the document or use this space to emphasize a key point. To place this text box anywhere on the page, just drag it.]

Grid support voltage setting is user specific based on sell back amount vs. reserve capacity

Note: XW Pro only - Make sure State of Charge Control is Enabled

53V

60 Amp Per Eflex

55 Amp Per Eflex

XW Pro only: Enable Fault on loss of BMS Status / State of Charge Information

## Exhibit E

Note: Be sure to click apply”