## Calculator
Fortress String Sizing Tool |  | Project Quantity | Design Validation
Select Inverter Model | SolArk-15K | 1 | Valid
Select PV Module | Input Your Own | 20 | Valid
Select Battery | eFlex | 2 | #NAME?
Max Typical Rooftop Temperature (°F) | 165 |  | Valid
Min Record Temperature (°F) | 0 |  | Use the lowest temperature on record
Above 5000 ft | No |  | Valid
Three-phase | No |  | Valid
UL9540 | Yes |  | Valid
Battery Location | Outdoor |  | Valid
Third-Party Heating Recommended | Yes |  | Valid
Selected Panel | Input Your Own | Add Your Own
Panel Watts | 400 | 400
Panel Voc | 48.8 | 48.8
Panel Isc | 10.28 | 10.28
Panel Vmpp | 42.1 | 42.1
Panel Vcoef | -0.2% | -0.2%
Panel Icoef | 0.04% | 0.04%
Warranted Elevation (ft) | 6500 | 6500
Selected Inverter | SolArk-15K |  | Per MPPT | Max Panels | Max Strings | Max Panels Per String | Min Panels Per String
Solar Volts Max | 550
Solar kW Max | 19.2 |  | MPPT1 | 20 | 2 | 10 | 3
Battery kW (continuous) | 12 |  | MPPT2 | 20 | 2 | 10 | 3
Quantity Max | 10 |  | MPPT3 | 20 | 2 | 10 | 3
Battery Communication | Yes |  | MPPT4 | 0 | 0 | 0 | 0
Mppt1 Amps | 26 |  | Per Inverter | 48 | Max Solar Panels Per Inverter
Mppt2 Amps | 26
Mppt3 Amps | 26
Mppt4 Amps | 0
Vmpp Min | 150
Vmpp Max | 500
Three Phase | Yes
Transformer | No
Elevation (Ft) | 6800
Selected Battery | eFlex
Quantity Max | 30 |  | 3 | Minimum Batteries Required Per Design
kwh | 5.4
kW 30 minute | 5
kW 60 minute | 5
kW 90 minute | 3.5
kW 120 minute | 2.7
Outdoor Installations Allowed | Yes
UL9540 | Yes
Outdoor Cabinet Option | Yes
Warranted Elevation (ft) | 6800
Transformerless Inverter Derate Allowance | 1
Heater Included | No
Temp Derate Low | 50
Temp Warranty Low | 40
Temp Cutoff Low Charge | 32
Temp Cutoff Low Discharge | -4
Temp Storage Low | -14
Temp Storage Low SoC | 40%

## Solar Panels
Solar Models | Watts | VoC | Isc | Vmpp | Vcoef | Icoef | Warranted Elevation
Input Your Own | 400 | 48.8 | 10.28 | 42.1 | -0.2% | 0.04% | 6500
REC 410 Alpha | 410 | 49 | 10.35 | 42.7 | -0.24% | 0.04% | 6800
REC 400 Alpha | 400 | 48.8 | 10.28 | 42.1 | -0.24% | 0.04% | 6800
REC 390 Alpha | 390 | 48.6 | 10.22 | 41.5 | -0.24% | 0.04% | 6800

## Inverters
Inverter Models | Max PV Input Voltage (V) | Max Input Current mppt 1 (A) | Max Input Current mppt 2 (A) | Maximum Input current MPPT 3 | Maximum Input current MPPT 4 | Minimum Vmpp | Maximum Vmpp | Maximum PV Size (kW) | Maximum Battery kW | Maximum Parallel | Three-Phase | Transformer | Warranted Elevation | Battery_Inverter_Communication
ENVY-12K | 600 | 25 | 15 | 15 | 0 | 230 | 500 | 21 | 12 | 5 | Yes | No | 6800 | Yes
ENVY-10K | 600 | 25 | 25 | 0 | 0 | 170 | 500 | 15 | 10 | 5 | Yes | No | 6800 | Yes
ENVY-8K | 600 | 25 | 25 | 0 | 0 | 170 | 500 | 13 | 8 | 5 | Yes | No | 6800 | Yes
SolArk-15K | 550 | 26 | 26 | 26 | 0 | 150 | 500 | 19.2 | 12 | 10 | Yes | No | 6800 | Yes
SolArk-12k-500V | 550 | 18 | 18 | 18 | 0 | 150 | 500 | 13 | 9 | 10 | Yes | No | 6800 | Yes
SolArk-12k-450V | 450 | 20 | 20 | 20 | 0 | 150 | 500 | 13 | 9 | 10 | Yes | No | 6800 | Yes
SolArk 8k | 550 | 18 | 18 | 18 | 0 | 150 | 500 | 10 | 8 | 1 | No | No | 6800 | Yes
SolArk 5k | 550 | 18 | 18 | 0 | 0 | 150 | 500 | 7 | 5 | 1 | No | No | 6800 | Yes
Schneider Electric XW Pro 6848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 4 | Yes | Yes | 6800 | Yes
Schneider Electric XW+ 6848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 4 | Yes | Yes | 6800 | No
Schneider Electric XW+ 5548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 4 | Yes | Yes | 6800 | No
Schneider Electric SW 4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | No | Yes | 6800 | No
OutBack Power Radian 8048A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 4 | Yes | Yes | 6800 | No
OutBack Power Radian 4048A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | No | Yes | 6800 | No
OutBack Power SkyBox SBX 5048 | 500 | 15 | 15 | 15 | 0 | 150 | 500 | 7 | 5 | 2 | No | Yes | 6800 | No
OutBack Power VFXR 3648A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 4 | No | Yes | 6800 | No
OutBack Power FXR 3048A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | No | Yes | 6800 | No
SMA Sunny Island 6048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 10 | Yes | Yes | 6800 | Yes
SMA Sunny Island 4548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 10 | Yes | Yes | 6800 | Yes
Studer Innotec AJ 400-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 4 | Yes | No | 6800 | Yes
Studer Innotec AJ 700-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 4 | Yes | No | 6800 | Yes
Studer Innotec XTS 1400-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 4 | Yes | No | 6800 | Yes
Studer Innotec XTS 2600-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 4 | Yes | No | 6800 | Yes
Studer Innotec XTS 4000-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | Yes | No | 6800 | Yes
Studer Innotec XTS 6000-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | Yes | No | 6800 | Yes
Studer Innotec XTS 8000-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 4 | Yes | No | 6800 | Yes
Magnum / Sensata MS 4448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 1 | No | Yes | 6800 | No
Magnum / Sensata MS 4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | No | Yes | 6800 | No
Victron Energy Quattro 48/3000/35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 12 | Yes | Yes | 6800 | Yes
Victron Energy Quattro 48/5000/70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | Yes | Yes | 6800 | Yes
Victron Energy Quattro 48/10000/140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | Yes | Yes | 6800 | Yes
Victron Energy Quattro 48/15000/200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | Yes | Yes | 6800 | Yes

## Batteries
Battery Models | kwh | kW 30 minute | kW 60 minute | kW 90 minute | kW 120 minute | Maximum Parallel | Outdoor | UL9540 | External Cabinet Option | Warranted Elevation | Transformerless Inverter Derate Allowance | Included Heater | Temp Derate Low | Temp Warranty Low | Temp Cutoff Low Charge | Temp Cutoff Low Discharge | Temp Storage Low | Temp Storage SoC
eVault MAX | 18.5 | 12 | 9.2 | 9.2 | 9.2 | 20 | No | Yes | No | 6800 | 1.35 | No | 50 | 40 | 32 | -4 | -14 | 40%
eFlex | 5.4 | 5 | 5 | 3.5 | 2.7 | 30 | Yes | Yes | Yes | 6800 | 1 | No | 50 | 40 | 32 | -4 | -14 | 40%
LFP10 MAX | 10 | 6 | 5 | 5 | 5 | 2 | No | No | No | 3500 | 1.35 | No | 50 | 40 | 32 | -4 | -14 | 40%

## Comments
1. Design tool does not accomodate multiple kinds of charging equipment (i.e. inverter + charge controler, AC coupling)
2. Reviews are needed on third party product data, particularly on elevation data.